## Sheet1
Nr. crt. | Device | LoRa Device | Variable measured | Unit measure | Variable | Reporting interval (RI) | Interval dashboard | Grouping Interval dashboard | Alarms
1 | Energy meter general (modbus addr. 1) building A | modbus-a-adeunis | Active Power average | W | p_tot | 15 min | month to date | 1 hour | -
|  |  | Active Energy | kWh | e_tot | 30 min | month to date | 1 hour | -
|  |  | Voltage phase R | V | vr | 15 min | month to date | 1 hour | 195,5 > vr > 253 "Voltage R phase out of range"
|  |  | Voltage phase S | V | vs | 15 min | month to date | 1 hour | 195,5 > vs > 253 "Voltage S phase out of range"
|  |  | Voltage phase T | V | vt | 15 min | month to date | 1 hour | 195,5 > vt > 253 "Voltage T phase out of range"
2 | Energy meter (modbus addr. 2) building A Takata * |  | Active Power average * | W | p_takata * | 15 min | - | - | -
|  |  | Active Energy * | kWh | e_takata * | 30 min | - | - | -
3 | Energy meter general (modbus addr. 1) building B | modbus-b-adeunis | Active Power average | W | p_tot | 15 min | month to date | 1 hour | -
|  |  | Active Energy | kWh | e_tot | 30 min | month to date | 1 hour | -
|  |  | Voltage phase R | V | vr | 15 min | month to date | 1 hour | 195,5 > vr > 253 "Voltage R phase out of range"
|  |  | Voltage phase S | V | vs | 15 min | month to date | 1 hour | 195,5 > vs > 253 "Voltage S phase out of range"
|  |  | Voltage phase T | V | vt | 15 min | month to date | 1 hour | 195,5 > vt > 253 "Voltage T phase out of range"
8 | Thermometer office A | therm-a-office-adeunis-comfort2 | Temperature Humidity Low Battery | oC % true/false | temperature humidity low_bat | 15 min | month to date | 1 hour | temperature > 25 "Temperature in the Office A too high!" temperature < 19 "Temperature in the Office A too low" Office A Thermometer battery low. Replace battery!
9 | Thermometer office B | therm-b-office-adeunis-comfort2 | Temperature Humidity Low Battery | oC % true/false | temperature humidity low_bat | 15 min | month to date | 1 hour | temperature > 25 "Temperature in the Office B too high!" temperature < 19 "Temperature in the Office B too low" Office B Thermometer battery low. Replace battery!
10 | Thermometer fridge | ext-therm-fridge-adeunis-temp | Temperature Low Battery | oC true/false | temperature low_bat | 15 min | month to date | 1 hour | temperature > -5 "Temperature in Refrigerator too high!" Refrigerator Thermometer battery low. Replace battery!
11 | Relay contact A | contact-a-adeunis-drycontact | Event counting Time duration Low Battery | number sec true/false | count duration low_bat | instant 15 min 15 min | month to date | 1 hour
11 | Relay contact B | contact-b-adeunis-drycontact | Event counting Time duration Low Battery | number sec true/false | count duration low_bat | instant 15 min 15 min | month to date | 1 hour
Misc. and other alarms:
1 | * Used only for calculation of energy & power
2 | TR > reporting + 1 min. | "Sensor <nume variabilă> inactive!"
3 | Energie = 0 (any variable type e_x) | "Meter <e_nume> inactive!"